## About
Structural design · RC modelling & detailing · Steel detailing
Deep beam
Simply supported deep beams · strut-and-tie, EN 1992-1-1 §6.5, §9.7 · UK NA / PN-EN
Reference | NAE-RC-044 · version 1.0
Standards | BS EN 1992-1-1:2004 with UK NA · PN-EN 1992-1-1:2008 with Polish NA (NDP sources listed on the NDP sheet)
National Annex | Selectable: UK NA to BS EN 1992-1-1 or Polish NA to PN-EN 1992-1-1
Issued | 30 October 2026
What it does
Design of a simply supported deep beam (span less than three times the depth, 5.3.1(3)) under a uniformly distributed load and a point load at midspan by a strut-and-tie model: tie force and bars, the support (CCT) and loaded (CCC) nodes and bearings, the bottle-shaped struts and their splitting force, the anchorage of the tie from the node face and the web mesh of 9.7.
How to use
1. Open the Calculation sheet and select the National Annex. 2. Fill in the shaded input cells. Everything else is calculated. 3. Read the Results block; every step below it quotes its clause. Print or save as PDF for your calculation package.
Scope and limitations
Rectangular beam of constant width, one span on two equal bearings, loads on the top face: a design UDL wEd over the span between bearing centres (include the self weight) and a design point load FEd at midspan on a plate as wide as the beam. Bearings as wide as the beam. Two trusses share one tie on the centroid of the bottom bars and one top chord: the UDL of each half span goes down a strut from a node at l/4, the point load down two struts from a node under the plate. Lever arm z = min(z0; zel): z0 from a compression block at the top at k1 ν' fcd, b y0 k1 ν' fcd (de − y0/2) = M, and zel = min(0.2 (l + 2h); 0.6 l), the elastic deep-beam lever arm of CEB-FIP and CIRIA Guide 2 (extrapolated above l/h = 2, where z0 usually governs); de = min(h; l) − u, as above a height l the wall only carries load down. Top node depth y0 where z0 governs, else 2 (de − z). Struts no flatter than 26.6° (cot θ ≤ 2). Nodes to 6.5.4(4): at the support the two struts are taken as their resultant on a node of height 2u (Figure 6.27), bearing and strut face at k2 ν' fcd; at the top the plate (FEd / (a2 b) plus the whole UDL / b), the top chord and the strut faces at k1 ν' fcd, the point-load strut on a2/2 of the plate, the UDL node smeared over l/2; the top chord between the UDL nodes carries Rw (l/4) / z and the midspan section the whole T. Each strut is checked at 0.6 ν' fcd (6.5.2(2)) on its narrower end (conservative; the strut at the support on its share of the node face), and the splitting force (6.59) of a bottle (Figure 6.25 b) is carried by the mesh crossing the strut over H/2, the mesh shared by the two struts. Tie anchorage (8.4, as RC-001) from the inner face of the bearing (6.5.4(7)) within the end of the beam: straight, or for one layer a 90° bend up with the mandrel of Table 8.1N and (8.1) and a 5φ tail inside the mesh; bars above φlarge are flagged for 8.8; good bond, α3 = α4 = α5 = 1; between layers cd also ≤ half the clear gap. Mesh As,dbmin and spacing of 9.7; the horizontal mesh bars start a clear gap above the top tie layer. Cover: c ≥ φ (+ 5 mm for dg > 32) for bond (4.4.1.2) is checked; durability and fire cover are the user's. Crack widths, deflection, lateral stability of thin beams, loads hung from the bottom face, openings and continuous deep beams are not covered. Concrete classes up to C50/60, fyk ≤ 500 MPa. The second-generation EN 1992-1-1:2023 is not yet implemented.
Further reading and independent cross-check
• EN 1992-1-1, 5.3.1, 5.6.4, 6.5, 8.3, 8.4 and 9.7. • CIRIA Guide 2, The design of deep beams in reinforced concrete (lever arm zel). • fib Bulletin 61, Design examples for strut-and-tie models. • IStructE, Manual for the design of concrete building structures to Eurocode 2. NA Engineering is not affiliated with The Concrete Centre or CIRIA; their publications are referenced for information only.
About NA Engineering
NA Engineering is a structural engineering consultancy delivering structural design, reinforced concrete modelling and detailing, and steel detailing for residential, commercial, infrastructure, energy and refurbishment projects. We share tools like this one because good engineering should be transparent: every formula here is visible and referenced. If you need a design, a check or a full detailing package, talk to us.
Website | naengineering.uk
Email | adrian@naengineering.uk
Phone | +48 505 844 422
LinkedIn | linkedin.com/company/naengineering
Disclaimer
This spreadsheet is provided free of charge, as is, for use by competent engineers. It does not replace engineering judgement. The user is responsible for the input, for checking that the method suits the element being designed and for verifying the results. NA Engineering accepts no liability for any loss arising from its use. Sheets are password-protected and the workbook structure is locked so that the formulas and the NA Engineering details cannot be changed; only the shaded input cells can be edited.
Revision history
v1.0 | 30 Oct 2026 · First issue

## Calculation
Deep beam
NAE-RC-044 v1.0 · naengineering.uk · adrian@naengineering.uk · +48 505 844 422
Project |  | Job no.
Element |  | Made by
Date |  | Checked
Inputs · beam |  |  |  |  | Shaded cells only
| National Annex |  | UK NA (BS EN)
Table 3.1 | Concrete strength class |  | C32/40
3.2.2 | Reinforcement characteristic yield strength (≤ 500 MPa) | fyk | 500 | MPa
8.2(2) | Maximum aggregate size | dg | 20 | mm
| Beam width (thickness) | b | 450 | mm
| Overall depth | h | 1800 | mm
5.3.1(3) | Span between bearing centres (l < 3h: deep beam) | l | 4500 | mm
| End of the beam beyond the bearing centre (≥ a1/2) | e | 500 | mm
| Support bearing length (along the span) | a1 | 550 | mm
| Load plate length at midspan (along the span) | a2 | 600 | mm
4.4.1 | Nominal cover to the web mesh (≥ φ for bond; durability by the user) | cnom | 40 | mm
Inputs · reinforcement |  |  |  |  | Tie bars inside the vertical mesh bars
| Tie bars: diameter | φt | 20 | mm
| Tie bars: number in each layer | nt | 5
| Tie bars: layers (clear gap between layers max(φ; dg + 5; 20)) | nl | 2
9.7(3) | Tie bar ends |  | Straight
9.7(1) | Web mesh, vertical bars: diameter (outermost) | φv | 12 | mm
9.7(2) | Web mesh, vertical bars: spacing | sv | 125 | mm
9.7(1) | Web mesh, horizontal bars: diameter | φh | 12 | mm
9.7(2) | Web mesh, horizontal bars: spacing | sh | 125 | mm
Inputs · actions |  |  |  |  | ULS design values
| Uniformly distributed load over the span (with self weight) | wEd | 150 | kN/m
| Point load at midspan | FEd | 1500 | kN
Inputs valid and consistent
Your deep beam, to scale · elevation · struts (dashed), tie (solid) and nodes (red) of the two trusses
Results
| Deep beam l/h < 3 and strut model valid (θ ≥ 26.6°) | l / h
| Tie As,req / As,prov (bars fit across the width) | As
Support node (CCT): bearing and strut face σ / k2 ν' fcd
Top node (CCC): load plate, top chord, strut faces σ / k1 ν' fcd
Struts: body 0.6 ν' fcd and splitting force on the mesh
Tie anchorage from the node face lbd / l_av (and the bend)
Web mesh 9.7: As,dbmin / As and spacing
No compression block fits at the top (z0 not real): increase b, h or the concrete class. θ < 26.6°: the beam is too shallow for this model. l/h ≥ 3: not a deep beam; design it as a beam (RC-004). Anchorage too short: lengthen the end of the beam, bend the bars up (9.7(3)) or use more, smaller bars.
Calculation · materials
2.4.2.4(1) | Partial factor, concrete | γc |  |  | NDP sheet
2.4.2.4(1) | Partial factor, reinforcement | γs |  |  | NDP sheet
3.1.6(1) | Coefficient on compressive strength (flexure) | αcc |  |  | NDP sheet
3.1.6(2) | Coefficient on tensile strength | αct |  |  | NDP sheet
8.8(1) | Large bar threshold | φlarge |  | mm | NDP sheet
6.5.4(4)a | k1 (CCC node) | k1 |  |  | NDP sheet
6.5.4(4)b | k2 (CCT node) | k2 |  |  | NDP sheet
Table 3.1 | Characteristic cylinder strength | fck |  | MPa
Table 3.1 | Mean tensile strength | fctm |  | MPa
3.1.6(1) | Design compressive strength αcc fck / γc | fcd |  | MPa
3.2.7 | Design yield strength | fyd |  | MPa
(6.57N) | ν' = 1 − fck / 250 (recommended; UK NA and PL NA.9) | ν'
(6.60) | CCC node limit k1 ν' fcd | σRd,CCC |  | MPa
(6.61) | CCT node limit k2 ν' fcd | σRd,CCT |  | MPa
(6.56) | Strut with transverse tension 0.6 ν' fcd | σRd,max |  | MPa
Calculation · geometry and actions
5.3.1(3) | Span to depth l / h (< 3: deep beam) | l/h
8.2(2) | Clear gap between tie bars and layers max(φt; dg + 5; 20) | amin |  | mm
Figure 6.27 | Tie centroid c + φv + φt/2 + (nl − 1)(φt + a_min)/2 | u |  | mm
| Effective depth h − u | d |  | mm
| Active depth min(h; l) − u | de |  | mm
| Reaction from the UDL wEd l / 2 | Rw |  | kN
| Reaction from the point load FEd / 2 | RF |  | kN
| Support reaction Rw + RF | R |  | kN
| Midspan moment wEd l² / 8 + FEd l / 4 | MEd |  | kNm
| Resultant of the struts at the support a = M / R | a |  | mm
Calculation · trusses
6.5.4(4)a | Compression block at k1 ν' fcd (de − √(de² − 2M / (b σRd,CCC))) | y0 |  | mm | N/A: no block fits
6.5 | Lever arm from the node z0 = de − y0/2 | z0 |  | mm
CIRIA Guide 2 | Elastic deep-beam lever arm min(0.2 (l + 2h); 0.6 l) | zel |  | mm
| Lever arm used min(z0; zel) | z |  | mm
| Top node depth (z0 governs: y0; else 2 (de − z)) | y |  | mm
6.5 | Tie force M / z (= compression through the section at midspan) | T |  | kN
6.5 | Top chord between the UDL nodes Rw (l/4) / z | Cw |  | kN
| UDL struts to l/4 tan θw = z / (l/4) | tan θw
| Point-load struts to l/2 tan θF = z / (l/2) | tan θF
| Flattest strut present tan θ ≥ 0.5 (θ ≥ 26.6°) | tan θ
| Angles θw, θF | θw |  | °
|  | θF |  | °
6.5 | UDL strut force Rw / sin θw | Fc,w |  | kN
6.5 | Point-load strut force RF / sin θF | Fc,F |  | kN
| Resultant at the support tan θ = z / a | tan θ
| Resultant angle | θ |  | °
6.5 | Resultant strut force R / sin θ | Fc |  | kN
Calculation · tie
| Required T / fyd | As,req |  | mm²
| Provided nl nt π φt² / 4 | As,prov |  | mm²
6.5.2(3) | Tie As,req ≤ As,prov | As,prov |  | mm²
| Side cover to the tie c + φv (bent bars: + φh, inside the mesh) | cs |  | mm
| Clear gap (b − 2 cs − nt φt) / (nt − 1) | a |  | mm
8.2(2) | Tie bars fit a ≥ a_min | a |  | mm
Calculation · nodes
6.5.4(4)b | Support bearing R / (a1 b) | σEd,1 |  | MPa
Figure 6.27 | Strut width at the support a1 sin θ + 2u cos θ | w1 |  | mm
6.5.4(4)b | Strut face at the support Fc / (b w1) | σEd,2 |  | MPa
(6.61) | Support node max(σEd,1; σEd,2) ≤ k2 ν' fcd | σEd |  | MPa
6.5.4(4)a | Load plate FEd / (a2 b) + wEd / b (whole UDL on the top face) | σEd,3 |  | MPa
6.5.4(4)a | Midspan node, vertical face T / (b y) (chord + point-load struts) | σEd,4 |  | MPa
6.5.4(4)a | UDL strut, top end y cos θw + (l/2) sin θw (smeared) | w2,w |  | mm
6.5.4(4)a | Point-load strut, top end y cos θF + (a2/2) sin θF | w2,F |  | mm
6.5.4(4)a | Strut faces at the top max(Fc / (b w2)) | σEd,5 |  | MPa
(6.60) | Top node max(σEd,3; σEd,4; σEd,5) ≤ k1 ν' fcd | σEd |  | MPa
Calculation · struts (0.6 ν' fcd on the narrower end; splitting (6.59))
| UDL strut: length √(a² + z²), a = l/4 | Hw |  | mm
Figure 6.25 | UDL strut: narrower end min(w1 share; w2) | aw |  | mm
6.5.2(2) | UDL strut: stress on the narrower end Fc / (b a) | σc,w |  | MPa
(6.59) | UDL strut: splitting force ¼ (1 − 0.7 a / (H/2)) Fc (≥ 0) | Ts,w |  | kN
6.5.3(3) | UDL: mesh 2 fyd (As,h sin²θ + As,v cos²θ) H/2 | TRd,w |  | kN
| Point-load strut: length √(a² + z²), a = l/2 | HF |  | mm
Figure 6.25 | Point-load strut: narrower end min(w1 share; w2) | aF |  | mm
6.5.2(2) | Point-load strut: stress on the narrower end Fc / (b a) | σc,F |  | MPa
(6.59) | Point-load strut: splitting force ¼ (1 − 0.7 a / (H/2)) Fc (≥ 0) | Ts,F |  | kN
6.5.3(3) | Point-load: mesh 2 fyd (As,h sin²θ + As,v cos²θ) H/2 | TRd,F |  | kN
6.5.2(2), 6.5.3(3) | Struts σc ≤ 0.6 ν' fcd; mesh shared Ts,w/TRd,w + Ts,F/TRd,F ≤ 1
Calculation · anchorage of the tie, 8.4
3.1.6(2) | Design tensile strength αct 0.7 fctm / γc | fctd |  | MPa
Figure 8.2 | Bond condition of the top layer (good: 1; else 0.7) | η1
(8.2) | Bond stress 2.25 η1 η2 fctd | fbd |  | MPa
8.4.3(2) | Stress in the bars T / As,prov (≤ fyd) | σsd |  | MPa
(8.3) | Basic length φ σsd / (4 fbd) | lb,rqd |  | mm
Figure 8.3 | Cover dimension min(a/2; layer gap/2; cs) | cd |  | mm
Table 8.2 | α1 (bend with cd > 3 φ: 0.7) | α1
Table 8.2 | α2 straight 1 − 0.15 (cd − φ)/φ; bend 1 − 0.15 (cd − 3φ)/φ (0.7 – 1.0) | α2
(8.6) | Minimum max(0.3 lb,rqd; 10 φ; 100) | lb,min |  | mm
(8.4) | Design anchorage length max(α1 α2 lb,rqd; lb,min) | lbd |  | mm
6.5.4(7) | Available a1/2 + e − c − φv (bearing face to bar end) | lav |  | mm
9.7(3) | Anchorage lbd ≤ l_av | lbd |  | mm
8.3 | Bend: bar force σsd π φ² / 4 (full force, conservative) | Fbt |  | kN
8.3 | Bend: ab = min(half the bar centres; cs + φ/2) | ab |  | mm
Table 8.1N, (8.1) | Bend: mandrel max(4φ or 7φ; Fbt (1/ab + 1/(2φ)) / fcd) | φm |  | mm
Figure 8.1 b | Bend: top of the 5φ tail y_top + φm/2 + φ + 5φ | ytail |  | mm
8.3, 8.4.1 | Bend: one layer, tail top ≤ h − c − φv (straight bars: n/a) | ytail |  | mm
Calculation · web mesh, 9.7
9.7(1) | As,dbmin / Ac (each face and direction) |  |  |  | NDP sheet
9.7(1) | Lower bound (0 = none) |  |  | mm²/m | NDP sheet
9.7(1) | Minimum per face max(ratio · b · 1000; lower bound) | As,dbmin |  | mm²/m
| Horizontal bars per face π φh² / 4 · 1000 / sh | As,h |  | mm²/m
| Vertical bars per face π φv² / 4 · 1000 / sv | As,v |  | mm²/m
9.7(2) | Maximum spacing min(2b; 300) | smax |  | mm
8.2(2) | Minimum clear gap, horizontal bars max(φh; dg + 5; 20) | ah,min |  | mm
8.2(2) | Minimum clear gap, vertical bars max(φv; dg + 5; 20) | av,min |  | mm
9.7(1), (2) | As,h and As,v ≥ As,dbmin; sh, sv ≤ smax; clear gaps ≥ a_min | As |  | mm²/m
| Vertical bars per face (drawn) | nv
| Horizontal bars per face (drawn) | nh
The tie bars sit inside the vertical mesh bars, which wrap under them as U-bars (cover c to the mesh). Anchor the tie for its full force from the inner face of each bearing (6.5.4(7), 9.7(3)); the available length is the straight run to the bar end, which for a bend is the outer face of its upstand (Figure 8.1 b). Concentrated loads hung from the bottom face need their own hanger reinforcement. The mesh carries the splitting force of the bottle-shaped struts (6.5.3(3)); the two struts' bottles overlap, so the mesh is shared: the sum of their utilisations is checked. Check crack widths where the exposure needs it (7.3).
Prepared with NA Engineering calculation tools · naengineering.uk · adrian@naengineering.uk. Free for use by competent engineers; see the About sheet for scope and disclaimer.

## Geometry (hidden)
Coordinates for the live drawings (mm). Generated - do not edit.
| outline | bearing 0 | bearing 1 | load plate | F | w line | w 0 | w 1 | w 2 | w 3 | w 4 | w 5 | w 6 | w 7 | tie layer 0 | tie layer 1 | tie layer 2 | vertical bars | horizontal bars | tie | strut w left | strut w right | strut F left | strut F right | strut top | nodes | nodes w | node F | dim | dim | dim | frame

## NDP
Nationally Determined Parameters
Values used by the Calculation sheet for the selected National Annex. Sources: UK NA to BS EN 1992-1-1:2004, Table NA.1; PN-EN 1992-1-1:2008, Załącznik krajowy NA. Edit only if your project specifies different values.
Parameter | Clause | UK NA | PL NA | Notes
Partial factor, concrete γc | 2.4.2.4(1) | 1.5 | 1.4 | Persistent & transient. UK NA: recommended; PL: NA.2, Table NA.2
Partial factor, reinforcement γs | 2.4.2.4(1) | 1.15 | 1.15 | UK NA: recommended; PL: NA.2, Table NA.2
αcc (compression in flexure / axial) | 3.1.6(1) | 0.85 | 1 | UK NA: 0.85; PL: recommended (NA.9)
αcc,pl (plain concrete, compression) | 12.3.1(1) | 0.6 | 0.8 | UK NA Table NA.1: 0.6; PL: recommended (NA.9)
αcc (shear and punching) | 3.1.6(1) | 1 | 1 | UK NA: 1.0 for other phenomena; PL: recommended (NA.9)
αct (design tensile strength) | 3.1.6(2) | 1 | 1 | Recommended value in both annexes
CRd,c numerator (CRd,c = value / γc) | 6.2.2(1), 6.4.4(1) | 0.18 | 0.18 | Recommended value in both annexes
k1 (axial stress term, punching) | 6.4.4(1) | 0.1 | 0.1 | Recommended value in both annexes
vRd,max factor (vRd,max = factor · ν · fcd) | 6.4.5(3) | 0.5 | 0.4 | UK NA: 0.5 ν fcd; PL: recommended value (NA.9), 0.4 ν fcd since EN 1992-1-1 AC:2010 (PN-EN 1992-1-1:2008/AC:2011)
kmax (vEd ≤ kmax · vRd,c at u1) | 6.4.5 | 2 | 1.5 | UK NA 6.4.5(3): 2 vRd,c. PL: no limit in PN-EN 1992-1-1:2008; 1.5 (A1:2014 recommendation) applied conservatively
φlarge (large bar threshold, mm) | 8.8(1) | 40 | 32 | UK NA: 40 mm; PL: 32 mm recommended (NA.9)
cot θ upper limit (variable strut) | 6.2.3(2) | 2.5 | 2 | UK NA: 2.5 (1.25 with axial tension); PL: NA.4, 1 ≤ cot θ ≤ 2.0
k1 (x/d limit, δ ≥ k1 + k2 xu/d) | 5.5(4) | 0.4 | 0.44 | UK NA for fyk ≤ 500 MPa; PL: recommended (NA.9)
k2 (x/d limit, εcu2 = 0.0035) | 5.5(4) | 1 | 1.25 | UK NA: 0.6 + 0.0014/εcu2; PL: 1.25(0.6 + 0.0014/εcu2)
Upper limit on the (310/σs) factor (0 = none) | 7.4.2(2) | 1.5 | 0 | UK NA Table NA.5 Note 5: (310/σs) or (500/fyk)(As,prov/As,req) ≤ 1.5; PL: none
L/d not to exceed 40 K (1 = applies) | 7.4.2(2) | 1 | 0 | UK NA Table NA.5 Note 6; not in EN text
φmin (longitudinal bars in columns, mm) | 9.5.2(1) | 12 | 6 | UK NA: 12 mm; PL: NA.6, 6 mm
k3 (crack spacing) | 7.3.4(3) | 3.4 | 3.4 | Recommended value in both annexes
k4 (crack spacing) | 7.3.4(3) | 0.425 | 0.425 | Recommended value in both annexes
k1 (concrete stress, characteristic; XD, XF, XS) | 7.2(2) | 0.6 | 1 | UK NA: recommended; PL: NA.5, k1 = 1.0
k2 (concrete stress, quasi-permanent; linear creep) | 7.2(3) | 0.45 | 0.45 | Recommended value in both annexes (UK NA; PL NA.9)
k3 (steel stress, characteristic) | 7.2(5) | 0.8 | 0.8 | Recommended value in both annexes (UK NA; PL NA.9)
k4 (steel stress, imposed deformation) | 7.2(5) | 1 | 1 | Recommended value in both annexes (UK NA; PL NA.9)
k1 (CCC node, σRd,max = k1 ν' fcd) | 6.5.4(4)a | 1 | 1 | Recommended value in both annexes (UK NA Table NA.1; PL NA.9)
k2 (CCT node, σRd,max = k2 ν' fcd) | 6.5.4(4)b | 0.85 | 0.85 | Recommended value in both annexes (UK NA Table NA.1; PL NA.9)
As,dbmin / Ac (deep beam mesh, each face and direction) | 9.7(1) | 0.002 | 0.001 | UK NA: 0.2 % in each face; PL: recommended 0.001 Ac (NA.9)
As,dbmin lower bound (mm²/m, each face and direction; 0 = none) | 9.7(1) | 0 | 150 | UK NA: 0.2 % only, no lower bound stated; PL: recommended 150 mm²/m (NA.9)